BPA dams: hourly operations data, 2018-2022

Prepared by Yi Lu for David Chassin (Eudoxys) and Bennet Meyers-Im (NLR)  |  Updated 2026-10-03

Hourly plant generation, flows and reservoir levels for the 14 Federal Columbia River Power System dams listed by David Chassin (email of 2026-10-01). Ten of them are the "Big 10" run-of-river dams (hourly data needed for 2020-2022); the files cover 2018-2022.

# 1. Files

| File | Content |
| --- | --- |
| dam_list.csv | Code, name, owner, river, state, Big 10 flag, data file, EIA plant id and EIA-860 nameplate capacity |
| USACE_CWMS_hourly/<CODE>_<Name>_hourly_2018_2022_UTC.csv | One file per dam, 43,824 hourly rows (2018-01-01 00:00 to 2022-12-31 23:00 UTC) |
| USACE_CWMS_hourly/data_dictionary.csv | Definition and unit of every column |
| USACE_CWMS_hourly/series_used.csv | Exact CWMS time series used for every dam and column, units, hours with data |
| manual_download_links.txt | One direct USACE download link per dam (same columns, UTC) for manual checking |
| power_MW_adjustments.csv | Change log: every hour where power_MW_adjust differs from power_MW (7 hours): file, hour, original and adjusted values, neighbouring hours, recording error |

# 2. Dams

| Code | Dam | Owner | River | State | Big 10 | Nameplate MW (EIA-860, 2020) |
| --- | --- | --- | --- | --- | --- | --- |
| ALF | Albeni Falls | USACE | Pend Oreille River | ID | no | 42.0 |
| BON | Bonneville | USACE | Columbia River | WA/OR | yes | 1162.0 |
| CHJ | Chief Joseph | USACE | Columbia River | WA | yes | 2456.2 |
| DWR | Dworshak | USACE | North Fork Clearwater River | ID | no | 465.0 |
| GCL | Grand Coulee | USBR | Columbia River | WA | yes | 6809.0 |
| HGH | Hungry Horse | USBR | South Fork Flathead River | MT | no | 428.0 |
| IHR | Ice Harbor | USACE | Snake River | WA | yes | 603.0 |
| JDA | John Day | USACE | Columbia River | WA/OR | yes | 2160.0 |
| LIB | Libby | USACE | Kootenai River | MT | no | 525.0 |
| LGS | Little Goose | USACE | Snake River | WA | yes | 810.0 |
| LWG | Lower Granite | USACE | Snake River | WA | yes | 810.0 |
| LMN | Lower Monumental | USACE | Snake River | WA | yes | 810.0 |
| MCN | McNary | USACE | Columbia River | WA/OR | yes | 990.5 |
| TDA | The Dalles | USACE | Columbia River | WA/OR | yes | 1819.7 |

Grand Coulee and Hungry Horse are owned by the U.S. Bureau of Reclamation (USBR), the other 12 by the U.S. Army Corps of Engineers (USACE). BPA markets the power of all 14; their operational data is kept in the USACE Northwestern Division CWMS database.

# 3. Columns

| Column | Description | Unit | CWMS parameter | Dams with data |
| --- | --- | --- | --- | --- |
| datetime_utc | Timestamp (UTC, hour-ending) |  |  | all 14 |
| power_MW | Plant total generation, hourly | MW | Power.Total.1Hour.1Hour | all 14 |
| power_MW_adjust | Plant total generation after correcting obvious recording errors: identical to power_MW except 7 hours, listed in BPA_dams/power_MW_adjustments.csv. Added by the data compiler. | MW | (derived from power_MW) | all 14 |
| station_service_MW | Station service (plant auxiliary) power, hourly | MW | Power-StationService.Total.1Hour.1Hour | ALF BON CHJ DWR GCL HGH IHR JDA LGS LWG LMN MCN TDA |
| spinning_reserve_MW | Spinning reserve carried by the plant, instantaneous at the hour | MW | Power-SpinningReserve.Inst.1Hour.0 | ALF BON CHJ GCL HGH JDA LIB LWG TDA |
| capacity_available_MW | Available generating capacity, hourly | MW | Power-Capacity-Avail.Total.1Hour.1Hour | GCL |
| outflow_kcfs | Total outflow (generation + spill + other), hourly average | kcfs (1,000 cubic feet per second) | Flow-Out.Ave.1Hour.1Hour | all 14 |
| genflow_kcfs | Flow through turbines (powerhouse flow), hourly average | kcfs (1,000 cubic feet per second) | Flow-Gen.Ave.1Hour.1Hour | all 14 |
| spill_kcfs | Spillway flow, hourly average | kcfs (1,000 cubic feet per second) | Flow-Spill.Ave.1Hour.1Hour | all 14 |
| inflow_kcfs | Reservoir inflow, hourly average | kcfs (1,000 cubic feet per second) | Flow-In.Ave.1Hour.1Hour | DWR |
| forebay_elev_ft | Forebay (reservoir) water surface elevation, instantaneous at the hour | ft | Elev-Forebay.Inst.1Hour.0 | all 14 |
| tailwater_elev_ft | Tailwater water surface elevation, instantaneous at the hour | ft | Elev-Tailwater.Inst.1Hour.0 | all 14 |
| storage_kaf | Reservoir storage, instantaneous at the hour | kaf (1,000 acre-feet) | Stor.Inst.1Hour.0 | BON CHJ DWR GCL HGH IHR LIB LGS LWG LMN |

# 4. Source and method

Agency: U.S. Army Corps of Engineers, Northwestern Division, Corps Water Management System (CWMS).

Web interface (manual checks): https://www.nwd-wc.usace.army.mil/dd/common/dataquery/www/

Download service: https://www.nwd-wc.usace.army.mil/dd/common/web_service/webexec/getjson (timezone = GMT)

For every dam and column both the revised (CBT-REV) and the raw (CBT-RAW) series were downloaded; the revised one is used unless the raw one has more hours of data. Plant power REV is empty for 13 of 14 dams in 2018-2022, so power_MW is the raw series (Hungry Horse: revised).

All CWMS columns, including power_MW, are stored exactly as published (no unit conversion, no gap filling, no outlier removal). power_MW_adjust is an added column with 7 obvious recording errors corrected (section 7).

All timestamps are UTC and hour-ending: the value at HH:00 is the average or total over the hour HH-1:00 to HH:00 (for instantaneous quantities, the reading at HH:00).

# 5. Accuracy checks (details in VERIFICATION_REPORT.docx)

Every link in manual_download_links.txt was downloaded again and compared with the files: about 5.0 million values, 0 differences. power_MW is identical to the source; the 7 corrections are only in the added column power_MW_adjust.

Time stamps: The Dalles outflow matches the USGS gauge below the dam (14105700) at 0 h lag, confirming UTC and hour-ending labels.

Annual energy agrees with EIA-923 within about 1.5 % for most dam-years (CWMS is gross output, EIA is net).

# 6. Notes for use

Big 10 dams (column big_10 in dam_list.csv) are the priority set; David Chassin's request highlights hourly data for 2020-2022. The files cover the full project period 2018-2022.

power_MW is gross plant output (before station service). Net output = power_MW - station_service_MW.

Head (ft) = forebay_elev_ft - tailwater_elev_ft.

For analysis use power_MW_adjust; power_MW keeps the published values for reference. The two differ only in the 7 hours listed in power_MW_adjustments.csv. Gaps are left empty in both and are not filled.

# 7. Corrected recording errors

Every hour of power_MW at all 14 dams was screened for recording errors against the turbine flow (genflow_kcfs), which is measured independently.

A value is corrected only if (1) it is an isolated value: its two neighbouring hours agree with each other and the turbine flow in that hour is steady, so the plant did not actually change output; (2) it is at least 5 times larger or smaller than the output implied by the flow (flow x the dam's 7-day median MW per kcfs); and (3) a single recording error explains it - one extra digit, or a decimal point misplaced by 10 or 100 - with the reconstructed value within 5 % of the flow-implied output. Where two reconstructions fit about equally well (within 1 %), one is chosen and the other is listed.

7 values meet this rule. power_MW keeps the published value; power_MW_adjust holds the corrected value. power_MW_adjustments.csv lists each one with the file, the hour, the original and adjusted values, the neighbouring hours, the recording error and any equally close alternative. In every other hour power_MW_adjust equals power_MW.

| Dam | Hour (UTC) | power_MW (original) | Prev / next hour MW | MW implied by flow | power_MW_adjust | Recording error |
| --- | --- | --- | --- | --- | --- | --- |
| CHJ | 2018-01-30 07:00 | 12,131.0 | 1,447 / 1,093 | 1,202 | 1,213 | delete digit '1' at position 5 |
| CHJ | 2018-02-17 16:00 | 10,992.0 | 2,006 / 2,003 | 1,986 | 1,992 | delete digit '0' at position 2 |
| CHJ | 2018-03-18 15:00 | 10,936.0 | 847 / 1,195 | 1,075 | 1,093 | delete digit '6' at position 5 |
| GCL | 2018-06-25 12:00 | 27,620.0 | 2,435 / 3,345 | 2,748 | 2,762 | delete digit '0' at position 5 |
| GCL | 2018-09-25 01:00 | 22,284.0 | 2,093 / 2,284 | 2,273 | 2,284 | delete digit '2' at position 1 |
| GCL | 2018-10-28 20:00 | 18.1 | 1,683 / 1,471 | 1,889 | 1,810 | decimal point misplaced (x100) |
| GCL | 2022-11-28 11:00 | 16.9 | 1,549 / 2,076 | 1,663 | 1,690 | decimal point misplaced (x100) |

# 8. Known data issues

Grand Coulee: power_MW summed over each year is 8-12 % higher than the generation reported by USBR and EIA-923, although the turbine flow volume matches USBR exactly. The hourly pattern can be used as is; for absolute energy, scale to USBR's monthly gross generation (RISE series 5257: https://data.usbr.gov/catalog/4194/item/5257). Which source is authoritative is to be confirmed with BPA/USBR.

McNary: about 7 % above EIA-923 in 2021 and 2022 (within 1 % in 2018-2020).

Other dam-years more than 3 % from EIA-923: Hungry Horse 2018 (+6.6 %), 2019 (+3.1 %), 2021 (-5.4 %); Dworshak 2018 (-5.2 %).

spinning_reserve_MW has fewer than 25 hours of data at JDA, LWG and TDA; capacity_available_MW exists only for Grand Coulee and inflow_kcfs only for Dworshak.

Hours without power_MW and adjusted hours per dam:

| Dam | Hours in files | Hours without power_MW | Hours where power_MW_adjust differs |
| --- | --- | --- | --- |
| ALF | 43824 | 137 | 0 |
| BON | 43824 | 3 | 0 |
| CHJ | 43824 | 0 | 3 |
| DWR | 43824 | 139 | 0 |
| GCL | 43824 | 0 | 4 |
| HGH | 43824 | 114 | 0 |
| IHR | 43824 | 88 | 0 |
| JDA | 43824 | 14 | 0 |
| LIB | 43824 | 273 | 0 |
| LGS | 43824 | 96 | 0 |
| LWG | 43824 | 129 | 0 |
| LMN | 43824 | 117 | 0 |
| MCN | 43824 | 52 | 0 |
| TDA | 43824 | 37 | 0 |